ETF-HT Product Specification

Pre-insulated piping system designed for above ground or direct buried Low Temp systems up to 366°.

| Steam Carrier: | Schedule 40 A-106 Grade B Seamless Steel |
| --- | --- |
| Cond. Carrier: | Schedule 80 A-106 Grade B Seamless Steel |
| Inner Layer Insulation: | Carrier pipe insulation shall be 1 ½”” of Cal Sil with service temp up to 1200° |
| Outer Layer Insulation: | Polyurethane foam as per table 1with the following minimum characteristics: K Factor 0.14, Density 2.8 PCF, closed cell content 90-95% in conformance with ASTM C-591 completely filling the annular space between foam glass and the jacket. |
| Jacketing Material: | High density polyethylene (HDPE) casing made from a polyethylene resin compound qualified as Type III, Category 5, Class C conforming to ASTM D-1248. Jacket diameter and wall thickness shall be per attached sheet. |
| End Seal: | Mastic end Seals factory applied to pipe ends. |
| Insulation of Straight Joints: | After welding and hydro testing, Cal Sil is wrapped around joint, an HDPE rock shield is slid over the joint and sealed with a 4” heat shrink Tape, polyurethane foam is poured into joint. |
| Fittings: | All fittings are field insulated in the same manner as the joints. |
| Trenching: | Underground systems shall be buried in a trench of not less than 24 inches deeper than the top of the pipe jacket and not less than 18 inches wider than the combined O.D. of all piping systems. Backfill should be tamped compactly in place. No rock shall be used in the first foot of the backfill. To meet H-20 highway loadings, there must be 24 inches from top of jacket to grade of the compacted fill. |

Page 1 of 2

Table 1:                       Specified Carrier Pipe / HDPE Jacket

| Nominal Pipe Size | Inner Layer Insulation Thickness | Outer Layer Insulation Thickness | HDPE Jacket Size | Jacket Thickness |
| --- | --- | --- | --- | --- |
| 1” | 1.00 | 1.48 | 6.63 | 150 mils |
| 1 ¼” | 1.00 | 1.31 | 6.63 | 150 mils |
| 1 ½” | 1.00 | 1.19 | 6.63 | 150 mils |
| 2” | 1.50 | 1.17 | 8.00 | 150 mils |
| 2 ½” | 1.50 | 1.00 | 8.00 | 150 mils |
| 3” | 1.50 | 1.61 | 10.00 | 150 mils |
| 4” | 1.50 | 1.11 | 10.00 | 175 mils |
| 5” | 1.50 | 1.80 | 12.43 | 175 mils |
| 6” | 1.50 | 1.27 | 12.43 | 175 mils |
| 8” | 1.50 | 1.09 | 14.06 | 175 mils |
| 10” | 2.00 | 1.43 | 17.83 | 175 mils |
| 12” | 2.00 | 1.40 | 19.80 | 175 mils |

ENERGY TASK FORCE LLC WARRANTY

Energy Task Force LLC warrants its products only to the extent that it will replace those proved to have manufactured defects, within a one-year period from date of delivery. Energy Task Force must be provided an opportunity to inspect an alleged defective product and the installation application. This warranty does not provide for the expenses incurred for removal, re-installation or consequential damages arising from the defective material. There is no warranty other than that described above, and no one is authorized to issue any other warranty related to Energy Task Force LLC products.

Page 2 of 2